## BoQ1 (hidden)
Item Wise BoQ | [13 empty] | 15
BoQ_Ver3.0 | Item Wise | Normal | INR Only | INR
Select, Excess (+), Less (-)
Tender Inviting Authority: Director CSIR-IIIM, Canal Road Jammu
Name of Work: Modular Clean Room
Contract No: 12(296)/2020-P
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (DOMESTIC TENDERS - RATES ARE TO GIVEN IN RUPEES (INR) ONLY) (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder in Rs. P | Excise Duty Amount in INR Rs. P | GST Amount in INR Rs. P | Freight Charges ( Unloading & Stacking) in Rs. P | Any Other Taxes in Rs. P | Any Other Duties/Levies in Rs. P | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [32 empty] | TOTAL AMOUNT Without Taxes col (13) = (4) x (7) in Rs. P | TOTAL AMOUNT With Taxes col (14) = sum (8) to (13) in Rs. P | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 7 | 8 | 9 | 10 | 11 | 12 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 13 | 14 | 15
1 | ( HVAC- DIRECT EXPANSION SYSTEM ) | [53 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | Air Handling Unit | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | Supply, installation, testing and commissioning of Single Decker type double skin ( with High density Puff insulation ) Draw through/Blow thru type AHUs complete with thermal break profile consisting of mixing air plenum section, blower sections with DIDW blowers(supply blower), DX type coil, G-4 (pre filters) & F-7(Fine filters) (The velocity across filter & coils should not exceed 500 FPM), 'Zero leak/ very low leakage' Aluminium Supply Air dampers, Return Air damper, Unit base frame with VI pads, motor suitable with variable frequency drive(VFD excluded) .Supply Air Plenum section, access doors across each section as per approved design, drive set with coupling guard, vibration isolators, internal lights, limit switches, necessary instruments. Motor shall be of IE.2 rating. All gasket shall be food grade neoprene. Activated carbon filters (bamboo based) should be supplied to control the VOC level and it should have the following technical specifications CTC Capacity (NLT 30) Total Surface area (B.E.T.) m2/g (NLT-900) Bulk density kg/m3 (NLT-336) Ball Pan hardness (NLT 80.0) Particle Size , 4mm 90 mass% Moisture NMT 5% Iodine Value (mg/ml) (NLT-1000) Rested Period (NLT 5 year) Supporting test reports should be enclosed. | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.02 | Capacity :- 5000 CFM(125 SP,6 Row) - 11 TR | item3 | 1 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
3.02 | Capacity :- 2000 CFM(65 SP,6 Row) - 8.5 TR | item4 | 1 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
4.02 | AIR COOLED -DIRECT EXPANSION TYPE Outdoor Type
5.02 | Supply, installation, testing & commissioning of condensing units with Scroll Compressor for Temperature control with Green refrigerant , Motor, Air cooled Cooled condenser ,control wiring and all accessories as required and called for, microprocessor based automatic and safety controls, all mounted on a steel frame complete as per specifications. Motor shall be suitable for 415+ 10% 50 cycles. 3 phase AC supply. Isolator and starter sha ll be provided in the Control Panel which shall be compatible with BMS system as per of specifications. Lifting, shifting, connection, fixing chillers including spring type vibration isolator, Dryer, Expansion Valves , Sight Glass to be included in quoted price.
6.02 | Capacity : 11 TR | item7 | 1 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
7.02 | Capacity : 8.5 TR | item8 | 1 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
8.02 | Ducting
9.02 | Supply &Installation of Ducting made out of GI sheet 120GSM Coating with metallic flanges, 6mm Gasketing & all joints to be sealed with silicon sealants(Dow Corning- Grade 752 Clear) an d to be tested according to SMACNA Standards Class1 at site after installation with proper gasketing, supports complete with all necessary hardware, accessories, fittings and fixtures, as per description in individual items, technical specifications, drawings and instructions of the Engineer-In charge. 24 gauge (up to 18") G.I. Ducting,
10.02 | 22Gauge | item11 | 125 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
11.02 | 24 Gauge | item12 | 350 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
13.02 | Insulation
14.02 | Supplying and fixing of laminated aluminium foil of mat finish cross linked polyethylene foam insulation on existing duct after applying two coats of cold sitting adhesive (CPRX compound). The joints shall seal with 2mm. wide and 3mm.thick self-adhesive nitrile rubber tape insulation complete as per specifications and as required. aluminium tape on A/C Duct.
15.02 | Thickness:- 13 mm | item15 | 300 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
16.02 | Thickness:- 09 mm | item16 | 200 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
17.02 | Supply, Installation, Testing & Commissioning (SITC) of Volume control dampers with opposed blade Zero leak type. Supply, fix, balance, and commission louvre type smooth supply air duct dampers made of Galvanized iron , lever, fixing arrangement etc. The damper shall be with all necessary hardware, accessories, fittings, and fixtures, as per description in individual items, technical specifications, drawings, and instructions of the Engineer-In charge. | item17 | 3 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
18.02 | Housing , Hepa filter, Al Grill With Damper(S.A)
19.02 | Supply, installation, testing& commissioning of MS powder coated Hepa Filter housing Provision for 0.3 micron Filters, Housing made of 16 G ( 18G Powder Coated) CRCA powder coated with SS304.grill, GI damper and Provision should be given to operate damper from inside the room. DOP, Pressure drop across the filters ports to be provided in the Housing2'x2'x6'' Filter Cap.500 cfm Return air Terminal filter Flushed with Panel along with the 10 filter Damper powder coated with SS304. grill, and Provision should be given to operate GI damper from inside the room.2'x1'x2'' Filter Cap.200 cfm
21.02 | Size:- 610X610X150 HEPA | item20 | 7 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
22.02 | Size:- 450X450X150 HEPA | item21 | 3 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
23.02 | Size:- 305X305X150 HEPA | item22 | 2 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
24.02 | Return Air Grills with Dampers
25.02 | Supply, installation, testing& commissioning of powder coated perforated (65%) supply air grills made out of Powder Coated extrude d aluminium sheet and volume control damper with Pre Filter of 10 Micron.
26.02 | Size:- 600mm x 300 mm | item25 | 5 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
27.02 | Size:- 300mm x 300 mm | item26 | 5 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
28.02 | Canvas Connections/Flexible Connections
29.02 | Supply, fixing of Anti Bacterial Type canvas connection to fix AHU with duct. | item27 | 12 | nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
30.02 | Copper Piping
31.02 | Supply and Installation of Copper piping with insulation c/w fittings. Installation must be done with proper supporting fixtures and clamps.
32.02 | Dia 5/8 inch | item31 | 40 | Rmt |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
33.02 | Dia 1/2 inch | item32 | 40 | Rmt |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
34.02 | Ms Supporting Fixtures for Ducting’s with Proper Threaded rod , Anchor Fasteners and Wooden base etc | item33 | 500 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
35.02 | Electrical Panel
36.02 | Supplying, installation, testing and commissioning of dust, damp and vermin p0of free floor, indoor type standing factory built sheet steel enclosed modular construction extendable panel, suitable for operation on 415±10% volts, 50 Hz AC 3 phase 4 wire system fabricated out of suitable sized square tubular section and covered with CRCA sheet steel of 2mm thick for frame work and covers, 3mm thick for gland plates i/c cleaning & finishing complete with 7 tank p0cess for powder coating in app0ved shade, complete with Aluminium bus bars, inter-connection with solid copper conductorwires / aluminium strips, neutral links, earth bus etc. necessary metering p0tections & indications and mounted with the following as per drawing and technical specifications attached etc. Complete as required. Cont0l wiring with 1.5 sq.mm. PVC insulated FRLS copper conductor Single Core cable. Each starter should have remote cont0l and interlocking facilities including auto manual switch, NO/NC contacts for BMS cont0l etc.complete as required. The Panel should be IBMS compatible.(The starter should have auto manual operation to take signal f0m fire panel for automatic operation of fan in case of fire.)Electrical Control Panel for AHU Units should include Starter panel along with thermostat controlling module which can be integrated with Controller feedback signals. | item35 | 1 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
37.02 | Supply and Laying of Electrical cabling - Copper Conductor including thimbles, Lugs at termination and proper Supporting arrangement etc.
38.02 | 16sq.mmx4Core (Power Cabling ) | item37 | 20 | Rmt. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
39.02 | 10sq.mmx4Core (Power Cabling ) | item38 | 40 | Rmt. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
40.02 | 6sq.mmx3Core (Power Cabling ) | item39 | 30 | Rmt. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
41.02 | 4sq.mmx3Core (Power Cabling ) | item40 | 30 | Rmt. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
42.02 | 2.5sq.mmx3 Core (Structure Cabling ) | item41 | 60 | Rmt. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
43.02 | 1.5sq.mmx2 Core (Structure Cabling ) | item42 | 100 | Rmt. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
44.02 | 0.75sq.mmx2 Core | item43 | 50 | Rmt. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
45.02 | Supply & installation of Perforated Galvanized Covered cable tray or Race way including suspending from ceiling with MS angle, 0ds connection pieces, G.I. nut bolts, G.I. washers, fasteners etc. as required.
46.02 | Size :150mm x 25mm x 150mm | item45 | 30 | Rmt. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
47.02 | Size :200mm x 25mm x 200mm | item46 | 30 | Rmt. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
48.02 | Supply & Installation of Magnehelic guage with inbuilt Digital Feedback Output port and Analog Output Dial, Unit Fixed Inside SS-304 Box. | item47 | 6 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
49.02 | Clean Room Validation which includes velocity test, particle count test, DOP test etc./w all documentation of IQ, DQ, PQ etc. ii) HEPA filter leak test iii) Room differential pressure test verification, iv) Particle test for cleanliness, v) Air pattern smoke test. vi) Air velocity test. | item48 | 1 | lot |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
50.02 | Hot Water Generator – Design, Supply, Installation and Commissioning for suitable Hot water generator inclusive of electrical panel and water piping upto the desired unit and should be included with all accessories to maintain the Air capacity, Temperature (22+/-2 deg C) and RH (45-50%) whenever required.
51.02 | For 5000 CFM AHU | item50 | 1 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
52.02 | For 2000 CFM AHU | item51 | 1 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
53.02 | Supply, installation, testing and commissioning of Aluminium Powder coated Grills/Diffusers with coated damper at inlet mouth and proper fixing arrangement. Coating thickness should not be less than 80 micron.
54.02 | 595mm X 595mm , 6 Nos | item53 | 24 | Sqft |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
55.02 | 450 mm X 450 mm , 2 Nos | item54 | 6 | Sqft |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
56.02 | Clean Room Compatible Switch & Socket - Supply & installation of Clean room Compatible Electrical switch & socket with all accessories
57.02 | 1 phase (5/16 Amp Socket) | item56 | 20 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
58.02 | 3 phase | item57 | 3 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
59.02 | (PUF PANELS & ACCESSORIES)
60.02 | Wall PUF Panel (Powder Coated )
61.02 | Supply & Installation of modular Partition sandwiched panel with Powder Coated Sheet on both sides of 0.6mm thick POLYEURATHANE FOAM as an infill material of density not less than that of 40±2kg/m3 with/WITHOUT tongue & groove arrangement and all wall panel joints are filled with good grade of silicon sealant. Make : Synergy/GMP/RINAC
62.02 | Thickness: 80 mm ( Independent ) | item61 | 170 | sqmtr |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
63.02 | Built In Riser PUF Panel (Powder Coated )
64.02 | Supply, Installation, Testing& commissioning of bulit in riser PCGI puf panel of 80 mm thick for return air damper & Al. powder coated Grill.
65.02 | Thickness: 80 mm | item64 | 70 | sqmtr |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
66.02 | Ceiling Puff Panel (Powder Coated )
67.02 | Supply & Installation of modular portion sandwiched ceiling panels with Powder Coated Sheet on both sides of 0.6 mm thick POLYEURATHINE FOAM as an infill material of density not less than that of 40±2kg/m3 with/without tongue &groove arrangement and all ceiling panel joints are filled with good grade of silicon sealant.
68.02 | Thickness: 50 mm | item67 | 80 | sqmtr |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
69.02 | Door
70.02 | Supply & Installation of Door with 64mm thickness suitable to fix in PUF wall mounted made with Pre Painted 0.8mm thick PCGI Sheet on both sided with honeycomb craft paper as in fill, 1.2mm thick .PCGI Powder coated door frames totally flush with all accessories.
71.02 | Double door (D2)1200x2100mm - Emergency Door | item70 | 1 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
72.02 | Single door (D1)915x2100mm | item71 | 12 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
73.02 | Single door (D1)750x2100mm | item72 | 1 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
74.02 | Door Closer | item73 | 15 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
75.02 | PVC Coving
76.02 | Supply & installation of PVC Coving of R60 is being used to fill the gap between wall panel to false ceiling and also between wall panels to wall panel at corners.
77.02 | Horizontal Coving for wall to ceiling | item76 | 120 | Rmt. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
78.02 | Vertical Coving | item77 | 135 | Rmt. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
79.02 | 3D Corner Cove | item78 | 50 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
80.02 | Flashing
81.02 | Supply & installation of U-Type flashing for Bottom & Top of Puff Panel plus door | item80 | 300 | Rmt. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
82.02 | Supply & installation of L-Type flashing for Vertical & Horizontal corners. | item81 | 150 | Rmt. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
83.02 | View Glass
84.02 | Supply & Installation of tempered view panels to be fitted on the Partition wall of 80mm thickness with 2 nos (Double glazed) of 5mm thick glass totally flush to the partition wall. Periphery is totally sealed with silicon sealant.
85.02 | View Panel Size : 1000x1000mm | item84 | 6 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
86.02 | Epoxy
87.02 | Supply and application of Epoxy flooring 5mm thick including complete work as per Tender Specifications. | item86 | 80 | sqmtr |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
88.02 | Epoxy Coving
89.02 | Supply and application of Epoxy coving, R60 includes complete work as per Tender Specifications. | item88 | 130 | Rmt |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
90.02 | LIGHT FITTINGS
91.02 | Wiring for light point / call bell point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular type switch, phenolic laminated sheet or 2mm thick SS plate on wall puf panel, suitable size G.I. box and earthing the point with 1.5 sq. mm. FRLS PVC insulated copper conductor single core cable etc as required. | item90 | 24 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
92.02 | Clean room compatible Recess Mounted , Bottom operable type light fixtures ,
93.02 | 610 mm x 610 mm , 45 watt | item92 | 14 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
94.02 | 305 mm x 305 mm , 20 watt | item93 | 10 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
95.02 | Supply, Installation and Commissioning of Glass work- Partition 10 mm toughened glass with SS 316, frame, fittings and fixtures. Glass door accessories must be of Dorma or Hettich Make | item94 | 70 | Sq.Mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
96.02 | EQUIPMENTS
97.02 | STATIC PASS BOX
98.02 | Supply, installation, testing& commissioning of SS-304 Dynamic Pass box having both double door having electromagnetic interlocking One time one side only open to control cross contamination with having UV light as well fluorescent light.
99.02 | Size:- 600X600X600mm | item98 | 1 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
100.02 | CROSS OVER BENCH
101.02 | Supply, installation, testing& commissioning of cross over bench made SS-304, both side shoose storing rack and blocking cross contamination to unclassified to classified area .
102.02 | Size:- 1500X350X610mm | item101 | 2 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
103.02 | DYNAMIC PASS BOX
104.02 | Supply, installation of Dynamic pass box fabricated with SS-304, completely automatic by using magnetic interlocking, one door lock automatically when the other is opened. Hepa filter (Mini Pleated) with efficiency of 99.997% down to 0.3 micron to be installed on ceiling top and pre filter down to 10 micron with an efficiency of 90% to be installed at side bottom. Dynamically and statically balanced blower with motor suitable for class 100k to be installed with Dwyer make magnahelic gauge,1x36w florescent light. Doors shall be double skin doors made of SS with glass view panel UV Light of Philips/eq. make 1x30w,single phase.220v,50Hz along with UV meter hour meter shall be provided to have a check on burning hour of UV. light
105.02 | Size:- 305X305X305-DIGITAL DISPLAY | item104 | 3 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
106.02 | BIOSAFETY CABINET (STAINLESS STEEL) CLASS II, TYPE A-2.
107.02 | Class II Bio safety Cabinet Type A2 design. • Should include a germicidal UV lamp, set of arm rest, an electrical outlet and a support stand provided with levelling bases. • Size 4 feet width and the front window must have 8/ 10” sash opening with working surface of stainless steel 304. • Motor should be DC or ECM & must automatically adjust the airflow speed (balancing inflow and down flow) without the use of a damper to ensure continuous safe working conditions. • The microprocessor must display the inflow and down flow air velocities in real-time on an LED/LCD display. • Hepa Filter should be 99.995% MPPS(Most Penetrating Particle Size) • UV light must be programmable to allow for specific exposure times from 0 to 24 hours. Lightening power should >1100 lux(100fc);cabinet noise level must be less than 65 dB(A) • Cabinet should be NSF (National Sanitation Foundation) certified and certificate of the quoted model should be attached. • Power Consumption in Normal mode :200W ±10% • CE certified with Warranty of 3 year and optional extended warranty for 3 years • The supplier should have at least 20 installations Base of Bio safety in India. | item106 | 2 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
108.02 | Size:- 1200X600X600mm
109.02 | BGLS -206(HLF 2) Laminar Air Flow – Vertical
110.02 | Laminar air flow cabinets able to create particle free air of Class-II Standard. The cabinet is fabricated out of Stainless Steel (SS 304) Both interior and exterior. Laminar flow is based on principle of double filtration of air. Atmospheric air will be drawn through the Pre-filters by heavy duty blowers. Filtered air than passed through highly effective HEPA Filters with 99.97% efficiency for particulates of 0.3 micron or larger along with meter display, which can filter almost all air born contaminants such as dust, fungal spores, bacteria etc. Double filtered laminar flow air will blow horizontally/vertically through the working table at a nominal velocity or approx. 90 Fts/min. Heavy duty imported blowers dynamically balanced with 0.25 HP electric motor are mounted on shock resistant base of cabinet or anti-vibration pads, operate on 230 +/- 10 volts, 50 Hz AC supply. Shadow less uniform lighting is provided within working space (100 feet candles). Vertical – VLF 2 Working Area – 4 ft X 2ft X 2ft Size of HEPA Filter- 4ft X 2ft X 6ft No. of HEPA Filter – 01 No of Pre filter – 01 Illumination – 1X 40 W | item109 | 2 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
111.02 | Autoclave - Vertical Steam Sterilizer
112.02 | Construction: Triple Walled Model No. of walls: Three Output Result : Complete Dry Interior & Exterior: SS 304 Gasket : Joint less Neoprene Gasket Working Pressure: 15 – 20 psi Working Temperature :110°C to 129°C Controller based :PID controller Pressure display :Analog dial gauge Timer: Digital Timer with Alarm Hydraulic tested :Tested up to 40 psi Basket : Stainless steel wire mesh type basket Power supply : Single-phase/triple phase Safety features : Low water indicator, Automatic pressure switch, Steam release valve, spring-loaded safety valve, Over temperature protection 21 CFR controller: 21 CFR controllers & software with our Steam Sterilizer for real-time monitoring of the temperature and pressure. 21 CFR controllers come with a computer interface that gives you real-time recording without any manipulation. Our controller display digital temperature, digital pressure, digital timer, purging temperature, & F0 value. 21 CFR controllers come with many features required for Steam Sterilizer. Real-time printing, Real-time data logging, F0 Value 4 channel mapping, Real-Time chart, Digital Pressure display Fully automatic operation Diameter 500 mm X Height 760 mm , Volume 150 liters, Load 5kW | item111 | 1 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
113.02 | Autoclave - Horizontal Steam Sterilizer, Rectangular Shape
114.02 | Shape Rectangular Operating temperature 121°C -134 °C Operating pressure 15 to 25 psi Hydraulic tested on 40 psi Insulation High-Quality Glass wool Piping Stainless Steel 304 Chamber condensate line Moisture Trap Controller type NABL certified PID temperature controller, Digital timer controller with END cycle buzzer Sensor Calibrated PT 100 Heaters ISI mark immersion heaters LID SS 304 w/ Pressure locking device Radial locking system Chrome-plated MS Stand SS 304 Tray SS tray /Sliding Trolley option rectangular Power supply 440 Volts 50 Hz, Three Phase Diameter X Height (mm) 500X900 Volume (Liters) 175 Standard IS 3829,ISO,ASTM and CE PLC with HMI Delta, Siemens &amp; Eurotherm PLC with touch screen HMI for better user experience. PLC consists of data logging facility, preset programs, USB port, RS 232 port, Graph, Animation and real-time printing with time, pressure and temperature recording. Temperature Controller a microprocessor-based PID controller consists of temperature, timer with a buzzer alarm. The controller has a double LED display for set and process value with a time of 9999 minutes. 21 CFR Controllers 21 CFR controllers display F0 value with an online data recording facility without any manipulation. 15 minutes at 121.1 degrees give F0 value 15 points; it is an important factor these days in the sterilization of surgical instruments in the pharmaceutical industry. Pressure Controller The pressure controller cuts off the electrical supply of heaters when it reaches to set value. DOORS The sterilizer can be designed in a single door or double door with a radial locking provision. Negative or positive pressure doesn’t allow the door to open until it comes to atmospheric pressure. TROLLEY The trolley can be designed in stainless steel or Mild steel with SS wheels for easy mobility. The trolley is a very essential part of the horizontal sterilizer which saves material from contamination. Safety Features Moisture Trap, Emergency ON/OFF, Vacuum Breaker, Multi Port Valve, Low water indicator, Automatic pressure switch, Steam release valve, spring-loaded safety valve, Over temperature protection
115.02 | Anti Vibration Table
116.02 | Size L 900 mm X D 600 mm X H 900 mm | item113 | 1 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
117.02 | Full Height Cabinet for Storage with glass door, As per SEFA Norms
118.02 | Tall Vertical Storage Cabinet for keeping files (Size L 1000 mmX W 400 mm X H 2100 mm) Material of construction of under storage cabinet Storage cabinets are custom-designed to fit in the given space with enough shelves and compartments as deemed necessary to utilize maximum available space for keeping files, books etc. Material of construction: Cabinet made in thick GI construction with corrosion resistant powder-coating/speciality coating. Number of shelves as per the size. Cabinet doors are made of toughened glass for easy visibility of books/files inside the cabinets. Door handles are pull type anodized/SS with self-closing hinges 11 Wall Bench with overhead cabinets as per SEFA 8 M and SEFA | item115 | 4 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
119.02 | Wall Bench with overhead cabinets as per SEFA 8 M and SEFA 10 Norms
120.02 | L (mm) X B(mm) X H (mm) = (1200+900+1500+1800+2100) X 750 X 900, Material of construction - SS 304, along with Electrical raceway. | item117 | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
121.02 | Under benches for Wall bench As per SEFA 8M and SEFA 10 Norms
122.02 | On heavy duty SS castors, Dimension -L(mm) X B (mm) X H (mm) = 600X500X820 with two doors and one drawer | item119 | 6 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
123.02 | BOD Incubator (Refrigerated)
124.02 | • Standard temperature setting range 0°C up to 99.9°C . • Temperature Uniformity ±0.3 °C at 37 °C. • Control: The system should have Microprocessor PID Control Technology. • Volume: The system should be in the chamber volume range of 110 -150 Liters • Door Sealing: The system should have Secure 2-point door seal and eccentric hinge ensure maximum gasket compression for stable chamber temperature • Ventilation system: o Forced convection design which allows rapid temperature response rates, improves the Uniformity and reduces fluctuation. o Low noise during operation. o Ventilated stainless steel shelves contribute to uniform air circulation. • Heating Technology: The system should have Pre heating technology where there are no exposed heating elements located inside the chamber to ensure maximum user safety. • Access port: The system should have access port for temperature validation & mapping. • Defrosting system: The system should have Auto defrosting system, which should get activate regularly for a pre determined period • Disinfection System: The system should have UV disinfection system which should run after initial start-up or manual control • Exterior & Interior: The exterior of the system should be of Electro galvanized steel with Antimicrobial Coating for killing the surface bacteria & the interior should be of Stainless steel, grade 304 with two SS Shelves • Exterior Dimensions: Due to the space constraint the external dimension must not be higher than W × D × H = 32˝ × 33˝ × 41˝ • Data Logging: PC-based software package developed for remote monitoring, data logging and programming/device configuration should be included. • Machine must be supplied with validation certificates i.e. DQ, IQ, OQ, PQ • Machine must be EN ISO/IEC 17050-1:2010 and CE certified | item121 | 2 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
125.02 | CO2 Incubator
126.02 | • Temperature range Ambient +5°C to 45°C . • Temperature Uniformity ±0.3 °C at 37 °C. • Interior Volume: Minimum 170 L and must not be higher than 200 liters • CO2 control range: 0-20%. Control: Better than ±0.1%, measures with T/C sensor • Readability and Satiability at least 0.1%. • Stainless steel shelves and supports should be readily removable without tools for easy cleaning, autoclaving or adjustment. • Heat sterilization cycle of at least 140⁰C for 12 hours to safely kill all organisms within the chamber. • Built in system audible alarm should be activated if the outer door is opened during the Heat Sterilization cycle and the temperature is 60°C or greater to ensure safety in the lab. • The Microprocessor Control System should give clear cut written message for the errors, should guide through the cycle with start-up and cycle status messages during decontamination phase. • Post decontamination process, the system should return to normal operating status without the need for manual cleaning. • HEPA filtered chamber airflow. - 100% filtration of chamber air every 60 seconds to clean room particulate and air borne contamination to best air quality standards thereby providing constant protection against contaminations. • Built-in system with adjustable timeframe to notify the user when it’s time to replace the filter and should be easily removable without tools. • Uniform distribution of direct heat at every part of the inner chamber. • There should be microbiological filters on all gas inlets and outlets and sample ports to reduce the potential contamination sources. • Programmable tracking alarms for temperature and CO2. Alarms should be custom configurable. • All probes and sensors located inside the chamber should be easily located. • System should be compatible to 230V/50-60 Hz. • Machine must be EN ISO/IEC 17050-1:2010 and CE certified | item123 | 1 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
127.02 | GARMENT CABINET (SS)
128.02 | • Garment Cabinet (L900mm X W400mm X H2700mm) with UV light provision , HEPA filter, Pre filters and it should be connected with the HVAC system, Material of construction SS-304 with Glass windows on the doors along with lock and key facility on the door. Two Partition and Numbers of Shelves for Aprons Storage. | item125 | 1 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
129.02 | DUSTBINS (SS)
130.02 | • Provision for clean room dustbin made up of SS 304, electro polished, cover should be operated by Foot pedal, round in shape, size - H 15 inch X 10 inch Dia | item127 | 6 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
131.02 | Clean room Chair
132.02 | • As per the norms of the clean room application, ESD protection, should have leg support, height adjustable, castors on the legs, MOC – Stainless steel and cushion on sitting and back support without hand support, Should have proper stitching of the cushion and back outer cover (Stapler or pasting of the outer cover is not accepted) | item129 | 10 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
133.02 | Emergency Shower along with Eye wash
134.02 | • Floor Mounted Emergency shower with eye wash- Galvanized steel piping. Brass fittings and Elbows with anti-corrosive polyamide 11 coating, high-visibility yellow plastic. WATER INLET: 1 1/4" PRESSURE: Rec. 2 bar, Min. 1,5 Max. 8 bar. SHOWER -Showerhead in plastic ABS. Flow rate regulated at110 l/min OPERATION: Pull handle EYEWASH -Two high-flow aerated water spray heads at low pressure with automatic opening anti-dust cover. Eyewash assembly in plastic ABS. Eyewash bowl in plastic ABS, Flow rate regulated at 22 l/mi, OPERATION: Push handle, Dimensions: 75x20x25cm (Should follow the ANSI disability friendly standards) | item131 | 1 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
135.02 | ELECTRONIC SYSTEM
136.02 | FIRE ALARM SYSTEM
137.02 | Design, Supply, installation, testing& commissioning of following items in FIRE ALARM SYSTEM. As per the technical specification as well as drawing to cover each room of the Microbiology clean room area • Fire smoke detectors • Fire Alarm Panel. • Battery • Audible Visual devices Sounder (Hotter) • Heat Sensor • Manual Call Point • FRSL Armoured Cable (Make: Gloster) • 25 mm PVC conduit including all accessories complete as required • Pipe with all Necessary Fittings ( Jindal) 2.00 lot • Fire Extinguisher including all accessories completeas per technical specification are required | item134 | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
138.02 | Access Control System.
139.02 | SDesign, Supply, Installation, Testing, Commissioning & Handing over the Access Control System as follows: Supply, Installation , Testing and Commissioning of Micro processor based access 1 Door controller engineered with 32 bit CPU having capacity of 1 door to integrate with 4 Readers at Multiple locations, Expandable, Net workable. TCP/IP protocol compatible distributed Intelligence and inbuilt flash memory, having data base upto 40000 cards and support transaction buffer of 10000 transaction, 2 supervised inputs and 1 Nos of relay outputs for easy and reliable interface with the 3rd party systems. Complete with Digital Power supply etc as required. Can read both biometric and card. | item136 | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
140.02 | CCTV System
141.02 | Supply Installation, Testing & Commissioning of Network Video Recorder Supply Installation Testing & Commissioning of 42" LED Monitor, Full HD, , HDMI Port, Supply Installation, Testing & Commissioning of wall mounted 42U rack (for Control Room) Supply Installation, Testing & Commissioning of FRLS PVC conduit 25 mm Supply Installation, Testing & Commissioning of 4 pair Cat-6 Cable Supply Installation, Testing & Commissioning of 24 port loaded jack panel for CCTV cable termination in rack Supply Installation, Testing & Commissioning of 1.5mtr RJ-45 CAT-6 Patch cord for jack panel to switch connectivity 1. CAMERA DOME 2MP IP CAMERA WITH AUDIO - 8.00 Nos 2. IP CAMERA BULLET 2MPIP CAMERA WITH AUDIO -2.00 Nos 3. POE SWITCH 4CH NETGEAR ALL PORT GEGY AND 2 UPLINK ( or Equivalent make)- 4.HARD DISC 2 TB SURVEILLANCE 5.CONNECTER 6 NVR 4 CH WITH AUDIO 7.CCTV Camera Installation | item138 | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
142.02 | MISCELLANEOUS
143.02 | Dismantling and demolishing
144.02 | • Removal /shifting of old furniture, and accessories and others unserviceable by mechanical transport including loading, unloading and proper stacking within 300 mtr. lead as per direction of Engineer in-charge. (The contractor shall visit of site and study the scope in detail work before submitting tender) • Demolishing R.C.C. Slab/ Granite counter with brick masonry support by manual including stacking of steel bars and disposal of unserviceable material. • Demolishing brick work (9” brick masonry wall (2 nos.) including stacking of serviceable material and disposal of unserviceable material. If passable with consultation of Structure Engineer • Dismantling of ceramic floor tiles and as well as wall tiles as per site. • Dismantling of 12 mm thick gypsum board false ceiling or partition walls including stacking of serviceable materials. • Dismantling/ removal of aluminium partitions, doors, windows, fixed glazing including disposal of unserviceable material and stacking of serviceable material as directed by Engineer-in-charge. • Dismantling/ taking out existing water supply line and drainage system or C.I. or G.I pipes including excavation and refilling trenches. • Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means, including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge. Including all lifts involved. | item141 | 1 | job |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
145.02 | Repair or minor civil work
146.02 | • Cutting of Hole for AHU duct as per HVAC drawing as well as same to be Repair with brick masonry work. • Repairs to plaster of thickness 12 mm to 20 mm in patches of area after removal of wall tiles or damp proof area or any other space if required, including cutting the patch in proper shape, and preparing and plastering the surface of the walls complete, as per direction of Engineer-in-Charge. • Applying one coat of water thinnable cement primer of approved brand and manufacture on wall surface: • Construction of RCC foundation/ cement concrete work etc. for AHU and other outsider equipment cooling systems as per approved drawing and design | item143 | 1 | job |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
147.02 | AHU shed
148.02 | Supplying and fixing steel structural shed in built up tubular (4"/3"/2"/ round, square or rectangular hollow tubes etc.) including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. and painting complete. Fixing in pre-coated galvanised iron profile sheets (size, shape and pitch of corrugation as approved by Engineer-in-charge) 0.50 mm (+ 0.05 %) on top roof, side cover with angle iron support, welded mesh and related other allied work desired by Engineer -in- charge. Size of Shed (4.0 mtr. L X 4.40 mtr. W x 2.50 mtr. H) | item145 | 1 | job |  |  |  | Excess(+) | 1 | Full Conversion | INR |  |  | 0 | [37 empty] | 0 | 0 | INR Zero Only
Total in Figures | [51 empty] | 0 | 0 | INR Zero Only | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [7 empty] | % | [39 empty] | 0 | 0 | Zero Only
Quoted Rate in Words |  | INR Zero Only
Note on K14: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K15: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K13: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.

## Macros
Please Enable Macros to View BoQ information