## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Office of Superintending engineer (E),IIIM Jammu
Name of Work:Fire Alarm System at Main Building IIIM Jammu
Contract No:
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Supply, Installation, Testing & Commissioning of intelligent analog addressable photothermal detector complete with mounting base as required on False Ceiling / Below False Floor. Approved Makes:- JCI, Ansul,Gentz,Notifier. | BI01010001010000000000000515BI0100001113 | 750 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
2 | Supply, Installation, Testing & Commissioning of intelligent addressable thermal detector with rate of rise cum fixed temperature thermistor complete with base as required ce / on False Ceiling / Below False Floor Makes:- JCI, Ansul,Gentz,Notifier. | BI01010001010000000000000515BI0100001115 | 55 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
3 | Supply, Installation, Testing & Commissioning of addressable manual call point complete as required. Makes:- JCI, Ansul,Gentz,Notifier. | BI01010001010000000000000515BI0100001116 | 35 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
4 | Supply, Installation, Testing & Commissioning of fire control module complete as required. Makes:- JCI, Ansul,Gentz,Notifier. | BI01010001010000000000000515BI0100001117 | 30 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
5 | Supply, Installation, Testing & Commissioning of Fault Isolator Module complete as required. Makes:- JCI, Ansul,Gentz,Notifier. | BI01010001010000000000000515BI0100001118 | 60 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
6 | Supply, Installation, Testing & Commissioning of Hooter/Strobe with all required accessories for mounting complete as required.Makes:- JCI, Ansul,Gentz,Notifier. | BI01010001010000000000000515BI0100001119 | 24 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
7 | Supply, Installation, Testing & Commissioning of Repeater Panel having 320 Character/Touch screen LCD display with inbuilt reset, acknowledge and silence switches complete as required. Makes:- JCI, Ansul,Gentz,Notifier. | BI01010001010000000000000515BI0100001121 | 3 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
8 | Supply, Installation, Testing & Commissioning of Microprocessor based intelligent addressable main fire alarm panel, central perocessing unit with the following loop modules and capable of supporting not less than 240 devices(including detectors) and minimum 120 detectors per loop and loop length up to 2 Km, network communication card, minimum 320 character graphics/ LCD display with touch screen or other key boards and minimum 4000 events history log in the non volatile memory( EPROM), power supply unit,48 hrs back up with 24 sealed maintenance batteries with automatic charger. The panel shall have facility to connect printout log and facility to have seamless integration with analog/digital voice evacuation system and shall be complete with aqll accessories. The panel shall be compatible for IBMS system with open protocal BACnet/Modbus over IP complete with two loop panel. Makes:- JCI, Ansul,Gentz,Notifier. | BI01010001010000000000000515BI0100001122 | 3 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
9 | Supplying and laying of 2 x 1.5 sqmm fire alarm armoured cable 600/1000 V rated with annealed copper conductor having XLPE insulation, Steel wire armouring & FRLS outer sheath complete as required. Make Havells/Finolex/RR/ABC | BI01010001010000000000000515BI0100001123 | 8500 | mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
10 | Supplying and fixing of PVC conduit 25 mm, ISI make | 33 | 2700 | mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
11 | Supplying and fixing of PVC conduit 40 mm, ISI make | 333 | 600 | mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
Total in Figures | [51 empty] | 0 | 0 | INR Zero Only | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | Zero Only
Quoted Rate in Words |  | INR Zero Only

## Macros
Please Enable Macros to View BoQ information