## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineeri,IIIM Jammu
Name of Work:BOQ for Supplying, Installation, Testing and Commissioning of 800 amps LT Panel( 1 no) and 400 amps LT Panel at IIIM Jammu
Contract No:
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1.01 | Supplying, installation, commissioning and testing of 800 amps indoor LT panel with 16 SWG MS Sheet. The panel should be dust free with proper rubber gaskets. The panel should be floor mounted with BUS Bar chamber, Earthing point, interconnections with Copper wiring. The panel should be coated with 2 coats of enamel paint( Grey Shade) with designation of incoming and outgoing feeder as per detail below: A. Incoming MCCB 630 amps 4 pole, 36 K ( 1 no), outgoing 250 amps MCCB 4 pole, 50 K ( 2 nos), outgoing 100 amps MCCB 4 pole 25 K ( 6 nos), outgoing 63 amps MCCB 4 pole 25 K ( 5 nos), MCB 40 amps(8 nos), MCB single pole (12 nos) and indicators with AE make Ammeters and Voltmers. Make of MCCB should be L&T/Siemens only | BI01010001010000000000000515BI0100001113 | 1 | Nos | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.01 | Supplying, installation, commissioning and testing of 400 amps indoor LT panel with 16 SWG MS Sheet. The panel should be dust free with proper rubber gaskets. The panel should be floor mounted with BUS Bar chamber, Earthing point, interconnections with Copper wiring. The panel should be coated with 2 coats of enamel paint( Grey Shade) with designation of incoming and outgoing feeder as per detail below: A. Incoming MCCB 250 amps 4 pole, 50 K ( 1 no), outgoing 63 amps MCCB 4 pole, 25 K ( 6 nos), with indicators with AE make Ammeters and Voltmers. Make of MCCBS should be L&T/Siemens only | BI01010001010000000000000515BI0100001114 | 1 | Nos | 101 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2.01 | Supplying, Conveying and fixing spls. Including eart | item2 | 124.223 | Nos
3.01 | Dismantling of existing old 600 Amps LT Panel | BI01010001010000000000000515BI0100001115 | 1 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
4.01 | Earthing with Copper Earth plate 600mmx 600mmx 3 mm thick including accessories and providing measonary Enclosure with cover plate | BI01010001010000000000000515BI0100001116 | 1 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5.01 | Supplying and Laying 25 mm x 5 mm copper strip at 0.50 mtrs below ground as strip earth electrode | BI01010001010000000000000515BI0100001117 | 28 | mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | 0 | 0 | INR Zero Only | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | Zero Only
Quoted Rate in Words |  | INR Zero Only

## Macros
Please Enable Macros to View BoQ information