## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Director IIIM Jammu
Name of Work:"Upgradation/Renovation of Laboratory in backside Portion of Kissan Training Centre at Chatha Farm,CSIR-IIIM Jammu" Electrical Work.
Contract No:
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular type switch, phenolic laminated sheet, suitable size G.I. box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. make Havells/ABB/Polycab/Anchor | [53 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.1 | Group C |  | 110 | point |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2 | Wiring in existing conduit: Supply and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in existing surface/ recessed steel/ PVC conduit as requried . Make- Havells/RR/Anchor/Shalimar | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.1 | 2 x 1.5 sq.mm |  | 500 | mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
2.2 | 2 x 2.5 sq.mm |  | 300 | mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
2.3 | 2 x 4.0 sq.mm |  | 625 | mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.4 | 2 x 6.0 sq.mm |  | 325 | mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.5 | 4 x 10.0 sq.mm |  | 60 | mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
3 | Supplying and drawing plain 16/0.2 ( 0.5) twin flat flexible FR PVC insulated annealed copper conductor, unarmored telephone cable in the PVC sleeve of Suitable size. Make Dlink/Shalimar/Havells | [53 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
3.1 | Twin Flat |  | 200 | mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. Make- National/Satia/ISI marked (2mm thick) | [53 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4.1 | 20 mm (2mm thick) |  | 250 | mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
4.2 | 25 mm (2mm thick) |  | 550 | mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
4.3 | 40 mm (2mm thick) |  | 60 | mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
5 | Supplying and fixing following sizes of Modules, GI Box with Modular base and Cover plate for modular switches in recesess etc as required. Make- Anchor/Legrand/ABB
5.1 | 1 or 2 Module ( 75 x 75 MM ) |  | 40 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
5.2 | 3 Module ( 100 mm x 75 mm ) |  | 30 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
5.3 | 4 Module ( 125 mm x 75 mm) |  | 35 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
5.4 | 6 Module ( 200 mm x 75 mm ) |  | 45 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
6 | Supplying and fixing following Modular type switch/ socket on the existing Switch box/ cover including connections etc. as required. Make-Anchor/Havells/Carbtree
6.1 | 5/6 amps switch |  | 125 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
6.2 | 15/16 amps switch |  | 80 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
6.3 | 3 pin 5/6 amps socket outlet |  | 125 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
6.4 | 6 pin15/16 amps socket outlet |  | 80 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
6.5 | Telephone Socket outlet |  | 10 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
7 | Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. Make- Anchor/Havells/Crompton |  | 38 | nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
8 | Supplying and drawing of UTP 4 pair CAT 6 LAN Cable Single run in theexisting surface/ recessed steel/ PVC conduit as required. Dlink/Havells/Shalimar |  | 300 | mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
9 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/recess, complete with tinned copper bus bar, neutral bus bar,earth bar, din bar, interconnections, powder painted includingearthing etc. as required. (But without MCB/RCCB/Isolator) Makes- Havells/ABB/Schnider
9.1 | 8 way (4 + 24), Double door |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
10 | Supplying and fixing following way, single pole and neutral, sheetsteel, MCB distribution board, 240 volts, on surface/ recess,complete with tinned copper bus bar, neutral bus bar, earth bar,din bar, interconnections, powder painted including earthing etc.as required. (But without MCB/RCCB/Isolator) Make-Havells/L&T/Legrand/Schinder
10.1 | 12 way Double door |  | 12 | nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
11 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, “C”curve, miniature circuit breaker suitable for inductive load offollowing poles in the existing MCB DB complete with connections,testing and commissioning etc. as required. . Make-Havells/L&T/ABB/Indo
11.1 | Single pole |  | 80 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
11.2 | Single pole and neutral |  | 20 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
11.3 | Double pole |  | 18 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
12 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thickincluding accessories, and providing masonry enclosure with coverplate having locking arrangement and watering pipe of 2.7 metrelong etc. with charcoal/ coke and salt as required. |  | 1 | Nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
13 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metrebelow ground as strip earth electrode, including connection/terminating with nut, bolt, spring, washer etc. as required. (Jointingshall be done by overlapping and with 2 sets of brass nut bolt &spring washer spaced at 50mm) |  | 18 | mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
14 | supplying and fixing of 2'x2' recess mounted LED fixture with 25-30 watts lamp. Make- Havells/Philips/Crompton |  | 55 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
15 | Supply and fixing of wall mountain fan 16" . Makes-Havells/Crompton/Bajaj/Usha |  | 38 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
16 | Supplying and fixing of 63 amps MCB,TPN. Make-Havells/L&T/ABB/Indo |  | 8 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
17 | Supplying and fixing of 40 amps MCB,DP.. Make-Havells/L&T/ABB/Indo |  | 18 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
18 | Supplying and fixing MCB Box cover for covering 40 ampsMCB, DP. |  | 18 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
19 | Supplying and fixing of Metal Exhaust Fans 12 inches with Louvers. . Make-Havells/Crompton/Usha/Bajaj |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
20 | Supplying and fixing of 4 feet LED light 20 watt.. Make-Havells/Crompton/Philips/Bajaj |  | 15 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
21 | Supplying, installation, commissioning and testing of 300 amps outdoor LT panel with 16 SWG MS Sheet. The panel should be dust free with proper rubber gaskets. The panel should be floor mounted with BUS Bar chamber, Earthing point, interconnections with Copper wiring. The panel should be coated with 2 coats of enamel paint( Grey Shade) with designation of incoming and outgoing feeder as per detail below: A. Incoming MCCB 250 amps 4 pole, 50 K ( 1 no), outgoing 125 amps MCCB 4 pole, 25 K ( 2 nos), with indicators with AE make Ammeters and Voltmers with end terminations. Make of MCCBS should be L&T/Siemens only |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
22 | Supply of 3.5 X 185 sq.mm XLPE Cable,A2XFY . Makes- Havells/ABB/KEI/Shalimar.The job includes termination at Panels with lugs. |  | 175 | mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
23 | Supply of 3.5 X 70 sq.mm XLPE Cable,A2XFY . Makes- Havells/ABB/KEI/Shalimar.The job includes termination at Panels with lugs. |  | 35 | mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
24 | Laying of 3.5 X 185 sq.mm, XLPE Cable.Makes- Havells/ABB/KEI/Shalimar |  | 175 | mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
25 | Laying of 3.5 X 70 sq.mm, XLPE Cable.Makes- Havells/ABB/KEI/Shalimar |  | 35 | mtr. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
26 | RJ-25 Internet termination points . |  | 25 | nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
27 | Supply,Installation,Testing and commissioning of 400 amps heavyduty Changeover with side Handle alongwith cable end terminations. Make-HPL/Havells//INDO |  | 1 | nos |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
Total in Figures | [51 empty] | 0 | 0 | INR Zero Only | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | Zero Only
Quoted Rate in Words |  | INR Zero Only

## Macros
Please Enable Macros to View BoQ information